## Sheet1
VC1 | SAT Alb020 (bifi)
Loss diagram values
LossType | Variable | Loss[PC] | Energy after |  |  | DiffHor | 566.9
Global horizontal irradiation, for 12327.3 m² of collectors
MainEnergy | GlobHor |  | 1799.3 | kWh/m² | Global horizontal irradiation
MainEnergy | GlobInc | 29.61% | 2332.1 | kWh/m² | Global incident in coll. plane
DetailPC | FShdGl | -1.822% | 2289.6 | kWh/m² | Near Shadings: irradiance loss
DetailPC | FIAMGl | -1.608% | 2252.8 | kWh/m² | IAM factor on global
MainPC | ReflFrt | 0.2% | 2257.3 | kWh/m² | Ground reflection on front side
| Bifacial: Global horizontal irrad. on reference reflexive ground = 25004.7 m² | [5 empty] | 25004.7
MainEnergy | GlobGnd |  | 676.8 | kWh/m² | Global incident on ground
MainPC | ReflLss | -80% | 135.4 | kWh/m² | Ground reflection loss |  | 135.36
| irradiation on the rear side, renormalized to 12327.3 m² of collectors | [5 empty] | 12327.3 | 2.0284 | 274.5643 | 0.493
MainPC | BkVFLss | -59.96% | 109.9 | kWh/m² | View Factor for rear side |  | 109.9246
MainPC | DifSBak | 14.77% | 126.2 | kWh/m² | Sky diffuse on the rear side |  | 126.1593
MainPC | BeamBak | 0.002% | 126.2 | kWh/m² | Beam effective on the rear side |  | 126.1618
MainPC | BackShd | -4.999% | 119.9 | kWh/m² | Shadings loss on rear side |  | 119.855
MainEnergy | GlobBak |  | 119.9 | kWh/m² | Global Irradiance on rear side
| Bifaciality factor | 70% | 83.9 | kWh/m² | Useable irradiance on the rear side
MainEnergy | GlobEff |  | 2257.3 | kWh/m² | Effective irradiation on collectors
| Global effective energy |  | 2341.2 | kWh/m² | (front + back side)
| on an area of |  | 12327.3 | m² | of collectors
| Total energy on collectors |  | 28860385 | kWh | Total available irradiation
| Efficiency at STC |  | 20.79% |  | (One-diode model)
Array losses
MainEnergy | EArrNom |  | 6001062 | kWh | Array nominal energy (at STC effic.)
DetailPC | GIncLss | -0.339% | 5980702 | kWh | PV loss due to irradiance level
DetailPC | TempLss | -5.521% | 5650494 | kWh | PV loss due to temperature
DetailPC | ModQual | 0.75% | 5692873 | kWh | Module quality loss
DetailPC | LIDLoss | -1% | 5635944 | kWh | LID - Light induced degradation
DetailPC | MisLoss | -1.15% | 5571130 | kWh | Mismatch loss, modules and strings
DetailPC | MismBak | -0.512% | 5542630 | kWh | Mismatch for back irradiance
DetailPC | OhmLoss | -1.209% | 5475637 | kWh | Ohmic wiring loss
MainEnergy | EArrMPP |  | 5475636 | kWh | Array virtual energy at MPP
System losses
DetailPC | IL_Oper | -1.953% | 5368680 | kWh | Inverter Loss during operation (efficiency)
DetailPC | IL_Pmax | -0.469% | 5343512 | kWh | Inverter Loss over nominal inv. power
DetailPC | IL_Imax | 0% | 5343512 | kWh | Inverter Loss due to max. input current
DetailPC | IL_Vmax | 0% | 5343512 | kWh | Inverter Loss over nominal inv. voltage
DetailPC | IL_Pmin | 0% | 5343512 | kWh | Inverter Loss due to power threshold
DetailPC | IL_Vmin | 0% | 5343512 | kWh | Inverter Loss due to voltage threshold
DetailPC | IL_Nigh | -0.025% | 5342160 | kWh | Night consumption
MainEnergy | EOutInv |  | 5342160 | kWh | Available Energy at Inverter Output
Losses after the inverter
MainEnergy | E_Grid |  | 5342160 | kWh | Energy injected into grid